## SHORT CIRCUIT CAL_ORIGINAL
Title |  |  |  | : | SHORT-CIRCUIT CURRENT CALCULATIONS | [16 empty] | Designer |  |  | : | BMR
Project Name |  |  |  | : | XYZ | [16 empty] | Consultant |  |  | : | AEC
Location |  |  |  | : | KSA | [16 empty] | Department |  |  | : | Design
Date |  |  |  | : | FEB.17, 2019 | [16 empty] | Section |  |  | : | ELECTRICAL
Short-Circuit Current Calculations as per IEC-60909
1.0 | PURPOSE:
The purpose of short-circuit current calculations is to determine the short-circuit ratings which are used to select the
KA interrupting capacity of the circuit breakers which can open and clear the fault current quickly and safely without
damaging.
2.0 | CALCULATION FORMULA:
Fault point
Z
[5 empty] | Isc (KA) = ELV(L-L) / √3 x ΣZT | [9 empty] | ΣZT= |  |  |  | RT2 + XT2
| 2.1 | Utility Short-Circuit Current (USCC) :
[6 empty] | Uscc = |  | Utility Short-Circuit Power | [12 empty] | Xutility = |  | 0.995 x Zu
3 13.8 KV
[6 empty] | Rutility = |  | 0.1 Xutility | [6 empty] | Zu = |  |  | ELV(L-L) 2 x 1000
[18 empty] | Utility SCP | [5 empty] | Where: USCP=500000000
| 2.2 | Transformer (TR) :
[6 empty] | Note: |  | Transformer Cu losses & transformer %Z to be taken as per SEC data.
[6 empty] | RTR = |  | TR Losses x 1000 | [6 empty] | ZTR = |  |  | %ZTR |  | x | ELV(L-L) 2
[8 empty] | 3 x (TR IFL) 2 | [9 empty] | 100% x TRKVA
[6 empty] | XTR = |  |  | ZTR2- RTR2 | [5 empty] | TRIFL = |  |  | TR Rated Capacity
3 x ELV(L-L)
| 2.3 | Cables :
[6 empty] | RC= ρ |  | LC | [6 empty] | XC = |  |  | 0.096 x LC |  |  | Note: Use 0.096 mΩ/m for 60Hz systems & 0.08 mΩ/m for 50Hz.
(n) A
Where :
|  |  | ρ |  | Resistivity constant of Cu conductor = 23.69 mΩ.mm2/m and for AL conductor = 37.65 mΩ.mm2/m
|  |  | n |  | Number of cables per phase
|  |  | A |  | Cross-sectional area of conductor (mm2)
|  |  | Z |  | Impedance
|  |  | T |  | Total
|  |  | Isc |  | Symmetrical 3-phase short-circuit current (KA)
|  |  | R |  | Resistance
|  |  | X |  | Inductive Reactance
|  |  | LC |  | Cable Length (m)
|  |  | KA |  | Kilo Ampere or 1000 Ampere
|  |  | TR |  | Transformer
|  |  | C |  | Cable
|  |  | ELV |  | Low voltage
|  |  | IFL |  | Full Load Current (Amp.)
Short-Circuit Current Calculations as per IEC-60909
Transformer TR-1
LV Installation |  |  |  | Description | [7 empty] | R (mΩ) |  |  | X (mΩ) |  |  | RT (mΩ) |  | XT (mΩ) |  | Isc (KA) = ELV(L-L) / √3 x ΣZT |  |  |  |  | Selected KA
Utility Source |  |  |  |  | MV Network | [6 empty] | 0.03184 |  |  | 0.3184 | [6 empty] | 20.9185 |  |  |  |  | 21
|  |  |  | ZS | Medium Voltage |  |  |  |  | 13800
[5 empty] | Utility SCC (KA) |  |  |  |  | 20.9185
[5 empty] | Utility SCP (MVA) |  |  |  |  | 500
Transformer |  |  |  |  | Transformer KVA |  |  |  |  | 1500 |  | 0.99556 |  |  | 6.3221 |  |  | 1.0274 |  | 6.6405 |  | 34.3686 |  |  |  |  | 35
[5 empty] | % Z TR |  |  |  |  | 6
|  |  |  | ZTR | ELV(L-L) |  |  |  |  | 400
[5 empty] | TR Losses (W) |  |  |  |  | 14000
[5 empty] | TR IFL(Amp.) |  |  |  |  | 2165.0635
Main CB |  |  |  | ZCB | On Secondary Side of TR. | [6 empty] | Negligible |  |  | Negligible |  |  | Not Considered in Practice
Bus Bars |  |  |  | ZBB | LVDP | [6 empty] | Negligible |  |  | Negligible |  |  | Not Considered in Practice
LV Cable |  |  |  |  | Cables from LV SWGR to MDP | [6 empty] | 1.0671 |  |  | 2.4 |  |  | 2.0945 |  | 9.0405 |  | 24.8859 |  |  |  |  | 25
|  |  |  | ZC1 | Cable size (mm2) |  |  |  |  | 185
[5 empty] | No. of cable(s) / Ph. |  |  |  |  | 3
[5 empty] | Cable length (m) |  |  |  |  | 25
LV Cable |  |  |  |  | Cables from MDP to DPR | [6 empty] | 3.9483 |  |  | 3.84 |  |  | 6.0428 |  | 12.8805 |  | 16.2319 |  |  |  |  | 18
|  |  |  | ZC2 | Cable size (mm2) |  |  |  |  | 240
[5 empty] | No. of cable(s) / Ph. |  |  |  |  | 1
[5 empty] | Cable length (m) |  |  |  |  | 40
LV Cable |  |  |  |  | Cables from DPR to LPR | [6 empty] | 6.3173 |  |  | 3.84 |  |  | 12.3602 |  | 16.7205 |  | 11.1066 |  |  |  |  | 14
|  |  |  | ZC3 | Cable size (mm2) |  |  |  |  | 150
[5 empty] | No. of cable(s) / Ph. |  |  |  |  | 1
[5 empty] | Cable length (m) |  |  |  |  | 40
LV Cable |  |  |  |  | Cables from LPR to LPR1 | [6 empty] | 37.904 |  |  | 3.84 |  |  | 50.2642 |  | 20.5605 |  | 4.2525 |  |  |  |  | 10
|  |  |  | ZC4 | Cable size (mm2) |  |  |  |  | 25
[5 empty] | No. of cable(s) / Ph. |  |  |  |  | 1
[5 empty] | Cable length (m) |  |  |  |  | 40
IX
IMPEDANCE DIAGRAM:
[11 empty] | ZS | = | #REF!
[11 empty] | ZT2 | = | Z TRANSFORMER T2 @ 6% | [6 empty] | #REF!
[11 empty] | ZL1 | = | #REF!
[11 empty] | ZL7 | = | #REF!
[11 empty] | ZL7A |  | = | #REF!
ZL7A1
[11 empty] | F7A1 |  | (FAULT AT F7A1 PANELBOARD NG1)
CABLE IMPEDANCE (FOR LENGTH OF CABLE FROM MAIN BUS TO FAULT (F7A1)
|  | CABLE SIZE IS |  |  |  | 2 |  | SETS 4C X 25mm2 + 10mm2 XLPE/PVC COPPER CABLE
|  | LENGTH OF Cable | [6 empty] | = | 6 |  |  | METERS
|  |  |  | (Cable Resistance) Rc | [6 empty] | = | Cable Resistance | [7 empty] | Length of Cable (KM)
Sets of Cable
|  |  |  | (Cable Resistance) Rc | [6 empty] | = | #REF! | [7 empty] | 0.006
2
|  |  |  | (Cable Resistance) Rc | [6 empty] | = | #REF! |  |  |  | OHMS
|  |  |  | (Cable Reactance) Xc | [6 empty] | = | Cable Reactance | [7 empty] | Length of Cable (KM)
Sets of Cable
|  |  |  | (Cable Reactance) Xc | [6 empty] | = | #REF! | [7 empty] | 0.006
2
|  |  |  | (Cable Reactance) Xc | [6 empty] | = | #REF! |  |  |  | OHMS
|  |  |  | ( a ) | Total Impedance
[8 empty] | ZL7A1 |  |  | = | (ZPU-RC)2 |  |  | + |  | (ZPU-XC)2
[8 empty] | ZL7A1 |  |  | = | #REF! |  |  | + |  | #REF!
[8 empty] | ZL7A1 |  |  | = | #REF!
|  |  |  | ( b ) | Total Impedance based on resistance (ZPU-RC)
[9 empty] | ZPU-RC |  | = | Rc |  |  |  | x |  | Base kVA
[12 empty] | (Base kV)2 |  |  |  | x |  | 1000
[9 empty] | ZPU-RC |  | = | #REF! |  |  | x |  | #REF!
[12 empty] | #REF! |  |  | x |  | 1000
[9 empty] | ZPU-RC |  | = | #REF!
|  |  |  | ( c ) | Total Impedance based on reactance (ZPU-XC)
[9 empty] | ZPU-XC |  | = | Xc |  |  |  | x |  | Base kVA
[12 empty] | (Base kV)2 |  |  |  | x |  | 1000
[9 empty] | ZPU-XC |  | = | #REF! |  |  | x |  | #REF!
[12 empty] | #REF! |  |  | x |  | 1000
[9 empty] | ZPU-XC |  | = | #REF!
Total Impedance at (ZL7A1) = Impedance to main bus+Impedance of cable
|  |  |  | ( d ) | Total Impedance
[7 empty] | ZPU-ZL7A1(F7A1) |  |  |  | = | (ZPU-RC)2 |  |  | + |  | (ZPU-XC)2
[7 empty] | ZPU-ZL7A1(F7A1) |  |  |  | = | #REF! |  |  | + |  | #REF!
[7 empty] | ZPU-ZL7A1(F7A1) |  |  |  | = | #REF!
| ( e ) |  | Total per unit impedance thru fault F7A1
|  |  | ZPU-ZT |  | = | ZPU-ST |  |  | + |  | ZPU-ZL1 |  |  | + |  | ZPU-ZL7 |  |  | + | ZPU-ZL7A(F7A) |  |  | + | ZPU-ZL7A1(F7A1)
|  |  | ZPU-ZT |  | = | #REF! |  |  | + |  | #REF! |  |  | + |  | #REF! |  |  | + | 0.025702 |  |  | + | #REF!
|  |  | ZPU-ZT |  | = | #REF!
|  |  |  | ( f ) | Short Circuit Motor Contribution at 50%
[8 empty] | ZPU-M |  | = | KVA Base
4 x motor kVA
[8 empty] | ZPU-M |  | = | #REF!
[11 empty] | 4 | x | 800
[8 empty] | ZPU-M |  | = |  | #REF!
|  |  |  | ( g ) | Total Impedance to main bus of NG1 (ZPU-B(F7A1))
[8 empty] | ZPU-B(F7A1) |  |  | = | ZPU-ZT |  |  | x |  | ZPU-M
[12 empty] | ZPU-ZT |  |  | + |  | ZPU-M
[8 empty] | ZPU-B(F7A1) |  |  | = | #REF! |  |  | x |  | #REF!
[12 empty] | #REF! |  |  | + |  | #REF!
[8 empty] | ZPU-B(F7A1) |  |  | = | #REF!
|  |  |  | ( h ) | ISC AT FAULT CURRENT "F7A1" AT NG1
[8 empty] | ISCF7A1(S) |  |  | = | Base Ampere
ZPU-B(F7A1)
[8 empty] | ISCF7A1(S) |  |  |  | 0
#REF!
[8 empty] | ISCF7A1(S) |  |  | = |  | #REF! |  |  |  |  | Ampere
|  |  |  | ( i ) | TAKING INTO CONSIDERATION FOR ASYMMETRICAL
ISC AT FAULT CURRENT "F7A1" AT NG1
[8 empty] | ISCF7A1(A) |  |  | = | ISCF7A1(S) |  |  | x |  | 1.25
[8 empty] | ISCF7A1(A) |  |  | = | #REF! |  |  | x |  | 1.25
[8 empty] | ISCF7A1(A) |  |  | = |  | #REF! |  |  |  |  | Ampere
USE * 12 KA INTERRUPTING CAPACITY FOR MAIN BREAKER OF NG1
TYPICAL FROM NG1 TO NG11
IX
IMPEDANCE DIAGRAM:
[11 empty] | ZS | = | #REF!
[11 empty] | ZT2 | = | Z TRANSFORMER T2 @ 6% | [6 empty] | #REF!
[11 empty] | ZL1 | = | #REF!
[11 empty] | ZL7 | = | #REF!
ZL7B
[11 empty] | F7B |  | (FAULT AT F7B PANELBOARD NFDB)
CABLE IMPEDANCE (FOR LENGTH OF CABLE FROM MAIN BUS TO FAULT (F7B)
|  | CABLE SIZE IS |  |  |  | 2 |  | SETS 4C X 120mm2 + 70mm2 XLPE/PVC COPPER CABLE
|  | LENGTH OF Cable | [6 empty] | = | 5 |  |  | METERS
|  |  |  | (Cable Resistance) Rc | [6 empty] | = | Cable Resistance | [7 empty] | Length of Cable (KM)
Sets of Cable
|  |  |  | (Cable Resistance) Rc | [6 empty] | = | #REF! | [7 empty] | 0.005
2
|  |  |  | (Cable Resistance) Rc | [6 empty] | = | #REF! |  |  |  | OHMS
|  |  |  | (Cable Reactance) Xc | [6 empty] | = | Cable Reactance | [7 empty] | Length of Cable (KM)
Sets of Cable
|  |  |  | (Cable Reactance) Xc | [6 empty] | = | #REF! | [7 empty] | 0.005
2
|  |  |  | (Cable Reactance) Xc | [6 empty] | = | #REF! |  |  |  | OHMS
|  |  |  | ( a ) | Total Impedance
[8 empty] | ZL7B |  |  | = | (ZPU-RC)2 |  |  | + |  | (ZPU-XC)2
[8 empty] | ZL7B |  |  | = | #REF! |  |  | + |  | #REF!
[8 empty] | ZL7B |  |  | = | #REF!
|  |  |  | ( b ) | Total Impedance based on resistance (ZPU-RC)
[9 empty] | ZPU-RC |  | = | Rc |  |  |  | x |  | Base kVA
[12 empty] | (Base kV)2 |  |  |  | x |  | 1000
[9 empty] | ZPU-RC |  | = | #REF! |  |  | x |  | #REF!
[12 empty] | #REF! |  |  | x |  | 1000
[9 empty] | ZPU-RC |  | = | #REF!
|  |  |  | ( c ) | Total Impedance based on reactance (ZPU-XC)
[9 empty] | ZPU-XC |  | = | Xc |  |  |  | x |  | Base kVA
[12 empty] | (Base kV)2 |  |  |  | x |  | 1000
[9 empty] | ZPU-XC |  | = | #REF! |  |  | x |  | #REF!
[12 empty] | #REF! |  |  | x |  | 1000
[9 empty] | ZPU-XC |  | = | #REF!
Total Impedance at (ZL7B) = Impedance to main bus+Impedance of cable
|  |  |  | ( d ) | Total Impedance
[7 empty] | ZPU-ZL7B(F7B) |  |  |  | = | (ZPU-RC)2 |  |  | + |  | (ZPU-XC)2
[7 empty] | ZPU-ZL7B(F7B) |  |  |  | = | #REF! |  |  | + |  | #REF!
[7 empty] | ZPU-ZL7B(F7B) |  |  |  | = | #REF!
|  |  |  | ( e ) | Total per unit impedance thru fault F7B
[5 empty] | ZPU-ZT |  |  | = | ZPU-ST |  |  | + |  | ZPU-ZL1 |  |  | + |  | ZPU-ZL7 |  | + | ZPU-ZL7B(F7B)
[5 empty] | ZPU-ZT |  |  | = | #REF! |  |  | + |  | #REF! |  |  | + |  | #REF! |  | + | #REF!
[5 empty] | ZPU-ZT |  |  | = | #REF!
|  |  |  | ( f ) | Short Circuit Motor Contribution at 50%
[8 empty] | ZPU-M |  | = | KVA Base
4 x motor kVA
[8 empty] | ZPU-M |  | = | #REF!
[11 empty] | 4 | x | 800
[8 empty] | ZPU-M |  | = |  | #REF!
|  |  |  | ( g ) | Total Impedance to main bus of NFDB (ZPU-B(F7B))
[8 empty] | ZPU-B(F7B) |  |  | = | ZPU-ZT |  |  | x |  | ZPU-M
[12 empty] | ZPU-ZT |  |  | + |  | ZPU-M
[8 empty] | ZPU-B(F7B) |  |  | = | #REF! |  |  | x |  | #REF!
[12 empty] | #REF! |  |  | + |  | #REF!
[8 empty] | ZPU-B(F7B) |  |  | = | #REF!
|  |  |  | ( h ) | ISC AT FAULT CURRENT "F7B" AT NFDB
[8 empty] | ISCF7B(S) |  |  | = | Base Ampere
ZPU-B(F7B)
[8 empty] | ISCF7B(S) |  |  |  | 0
#REF!
[8 empty] | ISCF7B(S) |  |  | = |  | #REF! |  |  |  |  | Ampere
|  |  |  | ( i ) | TAKING INTO CONSIDERATION FOR ASYMMETRICAL
ISC AT FAULT CURRENT "F7B" AT NFDB
[8 empty] | ISCF7B(A) |  |  | = | ISCF7B(S) |  |  | x |  | 1.25
[8 empty] | ISCF7B(A) |  |  | = | #REF! |  |  | x |  | 1.25
[8 empty] | ISCF7B(A) |  |  | = |  | #REF! |  |  |  |  | Ampere
USE * 35 KA INTERRUPTING CAPACITY FOR MAIN BREAKER OF NFDB
IX
IMPEDANCE DIAGRAM:
[11 empty] | ZS | = | #REF!
[11 empty] | ZT2 | = | Z TRANSFORMER T2 @ 6% | [6 empty] | #REF!
[11 empty] | ZL1 | = | #REF!
[11 empty] | ZL7 | = | #REF!
[11 empty] | ZL7B |  | = | #REF!
ZL7B1
[11 empty] | F7B1 |  | (FAULT AT F7B1 PANELBOARD NF1)
CABLE IMPEDANCE (FOR LENGTH OF CABLE FROM MAIN BUS TO FAULT (F7B1)
|  | CABLE SIZE IS |  |  |  | 1 |  | SETS 4C X 35mm2 + 16mm2 XLPE/PVC COPPER CABLE
|  | LENGTH OF Cable | [6 empty] | = | 15 |  |  | METERS
|  |  |  | (Cable Resistance) Rc | [6 empty] | = | Cable Resistance | [7 empty] | Length of Cable (KM)
Sets of Cable
|  |  |  | (Cable Resistance) Rc | [6 empty] | = | #REF! | [7 empty] | 0.015
1
|  |  |  | (Cable Resistance) Rc | [6 empty] | = | #REF! |  |  |  | OHMS
|  |  |  | (Cable Reactance) Xc | [6 empty] | = | Cable Reactance | [7 empty] | Length of Cable (KM)
Sets of Cable
|  |  |  | (Cable Reactance) Xc | [6 empty] | = | #REF! | [7 empty] | 0.015
1
|  |  |  | (Cable Reactance) Xc | [6 empty] | = | #REF! |  |  |  | OHMS
|  |  |  | ( a ) | Total Impedance
[8 empty] | ZL7B1 |  |  | = | (ZPU-RC)2 |  |  | + |  | (ZPU-XC)2
[8 empty] | ZL7B1 |  |  | = | #REF! |  |  | + |  | #REF!
[8 empty] | ZL7B1 |  |  | = | #REF!
|  |  |  | ( b ) | Total Impedance based on resistance (ZPU-RC)
[9 empty] | ZPU-RC |  | = | Rc |  |  |  | x |  | Base kVA
[12 empty] | (Base kV)2 |  |  |  | x |  | 1000
[9 empty] | ZPU-RC |  | = | #REF! |  |  | x |  | #REF!
[12 empty] | #REF! |  |  | x |  | 1000
[9 empty] | ZPU-RC |  | = | #REF!
|  |  |  | ( c ) | Total Impedance based on reactance (ZPU-XC)
[9 empty] | ZPU-XC |  | = | Xc |  |  |  | x |  | Base kVA
[12 empty] | (Base kV)2 |  |  |  | x |  | 1000
[9 empty] | ZPU-XC |  | = | #REF! |  |  | x |  | #REF!
[12 empty] | #REF! |  |  | x |  | 1000
[9 empty] | ZPU-XC |  | = | #REF!
Total Impedance at (ZL7B1) = Impedance to main bus+Impedance of cable
|  |  |  | ( d ) | Total Impedance
[7 empty] | ZPU-ZL7B1(F7B1) |  |  |  | = | (ZPU-RC)2 |  |  | + |  | (ZPU-XC)2
[7 empty] | ZPU-ZL7B1(F7B1) |  |  |  | = | #REF! |  |  | + |  | #REF!
[7 empty] | ZPU-ZL7B1(F7B1) |  |  |  | = | #REF!
| ( e ) |  | Total per unit impedance thru fault F7B1
|  |  | ZPU-ZT |  | = | ZPU-ST |  |  | + |  | ZPU-ZL1 |  |  | + |  | ZPU-ZL7 |  |  | + | ZPU-ZL7B(F7B) |  |  | + | ZPU-ZL7B1(F7B1)
|  |  | ZPU-ZT |  | = | #REF! |  |  | + |  | #REF! |  |  | + |  | #REF! |  |  | + | 0.045348 |  |  | + | #REF!
|  |  | ZPU-ZT |  | = | #REF!
|  |  |  | ( f ) | Short Circuit Motor Contribution at 50%
[8 empty] | ZPU-M |  | = | KVA Base
4 x motor kVA
[8 empty] | ZPU-M |  | = | #REF!
[11 empty] | 4 | x | 800
[8 empty] | ZPU-M |  | = |  | #REF!
|  |  |  | ( g ) | Total Impedance to main bus of NF1 (ZPU-B(F7B1))
[8 empty] | ZPU-B(F7B1) |  |  | = | ZPU-ZT |  |  | x |  | ZPU-M
[12 empty] | ZPU-ZT |  |  | + |  | ZPU-M
[8 empty] | ZPU-B(F7B1) |  |  | = | #REF! |  |  | x |  | #REF!
[12 empty] | #REF! |  |  | + |  | #REF!
[8 empty] | ZPU-B(F7B1) |  |  | = | #REF!
|  |  |  | ( h ) | ISC AT FAULT CURRENT "F7B1" AT NF1
[8 empty] | ISCF7B1(S) |  |  | = | Base Ampere
ZPU-B(F7B1)
[8 empty] | ISCF7B1(S) |  |  |  | 0
#REF!
[8 empty] | ISCF7B1(S) |  |  | = |  | #REF! |  |  |  |  | Ampere
|  |  |  | ( i ) | TAKING INTO CONSIDERATION FOR ASYMMETRICAL
ISC AT FAULT CURRENT "F7B1" AT NF1
[8 empty] | ISCF7B1(A) |  |  | = | ISCF7B1(S) |  |  | x |  | 1.25
[8 empty] | ISCF7B1(A) |  |  | = | #REF! |  |  | x |  | 1.25
[8 empty] | ISCF7B1(A) |  |  | = |  | #REF! |  |  |  |  | Ampere
USE * 18 KA INTERRUPTING CAPACITY FOR MAIN BREAKER OF NF1
IX
IMPEDANCE DIAGRAM:
[11 empty] | ZS | = | #REF!
[11 empty] | ZT2 | = | Z TRANSFORMER T2 @ 6% | [6 empty] | #REF!
[11 empty] | ZL1 | = | #REF!
[11 empty] | ZL7 | = | #REF!
ZL7C
[11 empty] | F7C |  | (FAULT AT F7C PANELBOARD NRDB)
CABLE IMPEDANCE (FOR LENGTH OF CABLE FROM MAIN BUS TO FAULT (F7C)
|  | CABLE SIZE IS |  |  |  | 2 |  | SETS 4C X 300mm2 + 150mm2 XLPE/PVC COPPER CABLE
|  | LENGTH OF Cable | [6 empty] | = | 9 |  |  | METERS
|  |  |  | (Cable Resistance) Rc | [6 empty] | = | Cable Resistance | [7 empty] | Length of Cable (KM)
Sets of Cable
|  |  |  | (Cable Resistance) Rc | [6 empty] | = | #REF! | [7 empty] | 0.009
2
|  |  |  | (Cable Resistance) Rc | [6 empty] | = | #REF! |  |  |  | OHMS
|  |  |  | (Cable Reactance) Xc | [6 empty] | = | Cable Reactance | [7 empty] | Length of Cable (KM)
Sets of Cable
|  |  |  | (Cable Reactance) Xc | [6 empty] | = | #REF! | [7 empty] | 0.009
2
|  |  |  | (Cable Reactance) Xc | [6 empty] | = | #REF! |  |  |  | OHMS
|  |  |  | ( a ) | Total Impedance
[8 empty] | ZL4A |  |  | = | (ZPU-RC)2 |  |  | + |  | (ZPU-XC)2
[8 empty] | ZL4A |  |  | = | #REF! |  |  | + |  | #REF!
[8 empty] | ZL4A |  |  | = | #REF!
|  |  |  | ( b ) | Total Impedance based on resistance (ZPU-RC)
[9 empty] | ZPU-RC |  | = | Rc |  |  |  | x |  | Base kVA
[12 empty] | (Base kV)2 |  |  |  | x |  | 1000
[9 empty] | ZPU-RC |  | = | #REF! |  |  | x |  | #REF!
[12 empty] | #REF! |  |  | x |  | 1000
[9 empty] | ZPU-RC |  | = | #REF!
|  |  |  | ( c ) | Total Impedance based on reactance (ZPU-XC)
[9 empty] | ZPU-XC |  | = | Xc |  |  |  | x |  | Base kVA
[12 empty] | (Base kV)2 |  |  |  | x |  | 1000
[9 empty] | ZPU-XC |  | = | #REF! |  |  | x |  | #REF!
[12 empty] | #REF! |  |  | x |  | 1000
[9 empty] | ZPU-XC |  | = | #REF!
Total Impedance at (ZL7C) = Impedance to main bus+Impedance of cable
|  |  |  | ( d ) | Total Impedance
[7 empty] | ZPU-ZL7C(F7C) |  |  |  | = | (ZPU-RC)2 |  |  | + |  | (ZPU-XC)2
[7 empty] | ZPU-ZL7C(F7C) |  |  |  | = | #REF! |  |  | + |  | #REF!
[7 empty] | ZPU-ZL7C(F7C) |  |  |  | = | #REF!
|  |  |  | ( e ) | Total per unit impedance thru fault F4A
[5 empty] | ZPU-ZT |  |  | = | ZPU-ST |  |  | + |  | ZPU-ZL1 |  |  | + |  | ZPU-ZL7 |  | + | ZPU-ZL7C(F7C)
[5 empty] | ZPU-ZT |  |  | = | #REF! |  |  | + |  | #REF! |  |  | + |  | #REF! |  | + | #REF!
[5 empty] | ZPU-ZT |  |  | = | #REF!
|  |  |  | ( f ) | Short Circuit Motor Contribution at 50%
[8 empty] | ZPU-M |  | = | KVA Base
4 x motor kVA
[8 empty] | ZPU-M |  | = | #REF!
[11 empty] | 4 | x | 800
[8 empty] | ZPU-M |  | = |  | #REF!
|  |  |  | ( g ) | Total Impedance to main bus of NRDB (ZPU-B(F7C))
[8 empty] | ZPU-B(F7C) |  |  | = | ZPU-ZT |  |  | x |  | ZPU-M
[12 empty] | ZPU-ZT |  |  | + |  | ZPU-M
[8 empty] | ZPU-B(F7C) |  |  | = | #REF! |  |  | x |  | #REF!
[12 empty] | #REF! |  |  | + |  | #REF!
[8 empty] | ZPU-B(F7C) |  |  | = | #REF!
|  |  |  | ( h ) | ISC AT FAULT CURRENT "F7C" AT NRDB
[8 empty] | ISCF7C(S) |  |  | = | Base Ampere
ZPU-B(F7C)
[8 empty] | ISCF7C(S) |  |  |  | 0
#REF!
[8 empty] | ISCF7C(S) |  |  | = |  | #REF! |  |  |  |  | Ampere
|  |  |  | ( i ) | TAKING INTO CONSIDERATION FOR ASYMMETRICAL
ISC AT FAULT CURRENT "F7C" AT NRDB
[8 empty] | ISCF7C(A) |  |  | = | ISCF7C(S) |  |  | x |  | 1.25
[8 empty] | ISCF7C(A) |  |  | = | #REF! |  |  | x |  | 1.25
[8 empty] | ISCF7C(A) |  |  | = |  | #REF! |  |  |  |  | Ampere
USE * 42 KA INTERRUPTING CAPACITY FOR MAIN BREAKER OF NRDB
IX
IMPEDANCE DIAGRAM:
[11 empty] | ZS | = | #REF!
[11 empty] | ZT2 | = | Z TRANSFORMER T2 @ 6% | [6 empty] | #REF!
[11 empty] | ZL1 | = | #REF!
[11 empty] | ZL7 |  | = | #REF!
[11 empty] | ZL7C |  | = | #REF!
ZL7C1
[11 empty] | F7C1 |  | (FAULT AT F7C1 PANELBOARD NR1)
CABLE IMPEDANCE (FOR LENGTH OF CABLE FROM MAIN BUS TO FAULT (F7C1)
|  | CABLE SIZE IS |  |  |  | 1 |  | SETS 4C X 25mm2 + 10mm2 XLPE/PVC COPPER CABLE
|  | LENGTH OF Cable | [6 empty] | = | 12 |  |  | METERS
|  |  |  | (Cable Resistance) Rc | [6 empty] | = | Cable Resistance | [7 empty] | Length of Cable (KM)
Sets of Cable
|  |  |  | (Cable Resistance) Rc | [6 empty] | = | #REF! | [7 empty] | 0.012
1
|  |  |  | (Cable Resistance) Rc | [6 empty] | = | #REF! |  |  |  | OHMS
|  |  |  | (Cable Reactance) Xc | [6 empty] | = | Cable Reactance | [7 empty] | Length of Cable (KM)
Sets of Cable
|  |  |  | (Cable Reactance) Xc | [6 empty] | = | #REF! | [7 empty] | 0.012
1
|  |  |  | (Cable Reactance) Xc | [6 empty] | = | #REF! |  |  |  | OHMS
|  |  |  | ( a ) | Total Impedance
[8 empty] | ZL7C1 |  |  | = | (ZPU-RC)2 |  |  | + |  | (ZPU-XC)2
[8 empty] | ZL7C1 |  |  | = | #REF! |  |  | + |  | #REF!
[8 empty] | ZL7C1 |  |  | = | #REF!
|  |  |  | ( b ) | Total Impedance based on resistance (ZPU-RC)
[9 empty] | ZPU-RC |  | = | Rc |  |  |  | x |  | Base kVA
[12 empty] | (Base kV)2 |  |  |  | x |  | 1000
[9 empty] | ZPU-RC |  | = | #REF! |  |  | x |  | #REF!
[12 empty] | #REF! |  |  | x |  | 1000
[9 empty] | ZPU-RC |  | = | #REF!
|  |  |  | ( c ) | Total Impedance based on reactance (ZPU-XC)
[9 empty] | ZPU-XC |  | = | Xc |  |  |  | x |  | Base kVA
[12 empty] | (Base kV)2 |  |  |  | x |  | 1000
[9 empty] | ZPU-XC |  | = | #REF! |  |  | x |  | #REF!
[12 empty] | #REF! |  |  | x |  | 1000
[9 empty] | ZPU-XC |  | = | #REF!
Total Impedance at (ZL7C1) = Impedance to main bus+Impedance of cable
|  |  |  | ( d ) | Total Impedance
[7 empty] | ZPU-ZL7C1(F7C1) |  |  |  | = | (ZPU-RC)2 |  |  | + |  | (ZPU-XC)2
[7 empty] | ZPU-ZL7C1(F7C1) |  |  |  | = | #REF! |  |  | + |  | #REF!
[7 empty] | ZPU-ZL7C1(F7C1) |  |  |  | = | #REF!
| ( e ) |  | Total per unit impedance thru fault F7C1
|  |  | ZPU-ZT |  | = | ZPU-ST |  |  | + |  | ZPU-ZL1 |  |  | + |  | ZPU-ZL7 |  |  | + | ZPU-ZL7C(F7C) |  |  | + | ZPU-ZL7C1(F7C1)
|  |  | ZPU-ZT |  | = | #REF! |  |  | + |  | #REF! |  |  | + |  | #REF! |  |  | + | 0.017023 |  |  | + | #REF!
|  |  | ZPU-ZT |  | = | #REF!
|  |  |  | ( f ) | Short Circuit Motor Contribution at 50%
[8 empty] | ZPU-M |  | = | KVA Base
4 x motor kVA
[8 empty] | ZPU-M |  | = | #REF!
[11 empty] | 4 | x | 800
[8 empty] | ZPU-M |  | = |  | #REF!
|  |  |  | ( g ) | Total Impedance to main bus of NR1 (ZPU-B(F7C1))
[8 empty] | ZPU-B(F7C1) |  |  | = | ZPU-ZT |  |  | x |  | ZPU-M
[12 empty] | ZPU-ZT |  |  | + |  | ZPU-M
[8 empty] | ZPU-B(F7C1) |  |  | = | #REF! |  |  | x |  | #REF!
[12 empty] | #REF! |  |  | + |  | #REF!
[8 empty] | ZPU-B(F7C1) |  |  | = | #REF!
|  |  |  | ( h ) | ISC AT FAULT CURRENT "F7C1" AT NR1
[8 empty] | ISCF7C1(S) |  |  | = | Base Ampere
ZPU-B(F7C1)
[8 empty] | ISCF7C1(S) |  |  |  | 0
#REF!
[8 empty] | ISCF7C1(S) |  |  | = |  | #REF! |  |  |  |  | Ampere
|  |  |  | ( i ) | TAKING INTO CONSIDERATION FOR ASYMMETRICAL
ISC AT FAULT CURRENT "F7C1" AT NR1
[8 empty] | ISCF7C1(A) |  |  | = | ISCF7C1(S) |  |  | x |  | 1.25
[8 empty] | ISCF7C1(A) |  |  | = | #REF! |  |  | x |  | 1.25
[8 empty] | ISCF7C1(A) |  |  | = |  | #REF! |  |  |  |  | Ampere
USE * 12 KA INTERRUPTING CAPACITY FOR MAIN BREAKER OF NR1
IX
IMPEDANCE DIAGRAM:
[11 empty] | ZS | = | #REF!
[11 empty] | ZT2 | = | Z TRANSFORMER T2 @ 6% | [6 empty] | #REF!
[11 empty] | ZL1 | = | #REF!
[11 empty] | ZL7 |  | = | #REF!
[11 empty] | ZL7C |  | = | #REF!
ZL7C2
[11 empty] | F7C2 |  | (FAULT AT F7C2 PANELBOARD MCC-1)
CABLE IMPEDANCE (FOR LENGTH OF CABLE FROM MAIN BUS TO FAULT (F7C2)
|  | CABLE SIZE IS |  |  |  | 2 |  | SETS 4C X 300mm2 + 150mm2 XLPE/PVC COPPER CABLE
|  | LENGTH OF Cable | [6 empty] | = | 18 |  |  | METERS
|  |  |  | (Cable Resistance) Rc | [6 empty] | = | Cable Resistance | [7 empty] | Length of Cable (KM)
Sets of Cable
|  |  |  | (Cable Resistance) Rc | [6 empty] | = | #REF! | [7 empty] | 0.018
2
|  |  |  | (Cable Resistance) Rc | [6 empty] | = | #REF! |  |  |  | OHMS
|  |  |  | (Cable Reactance) Xc | [6 empty] | = | Cable Reactance | [7 empty] | Length of Cable (KM)
Sets of Cable
|  |  |  | (Cable Reactance) Xc | [6 empty] | = | #REF! | [7 empty] | 0.018
2
|  |  |  | (Cable Reactance) Xc | [6 empty] | = | #REF! |  |  |  | OHMS
|  |  |  | ( a ) | Total Impedance
[8 empty] | ZL7C2 |  |  | = | (ZPU-RC)2 |  |  | + |  | (ZPU-XC)2
[8 empty] | ZL7C2 |  |  | = | #REF! |  |  | + |  | #REF!
[8 empty] | ZL7C2 |  |  | = | #REF!
|  |  |  | ( b ) | Total Impedance based on resistance (ZPU-RC)
[9 empty] | ZPU-RC |  | = | Rc |  |  |  | x |  | Base kVA
[12 empty] | (Base kV)2 |  |  |  | x |  | 1000
[9 empty] | ZPU-RC |  | = | #REF! |  |  | x |  | #REF!
[12 empty] | #REF! |  |  | x |  | 1000
[9 empty] | ZPU-RC |  | = | #REF!
|  |  |  | ( c ) | Total Impedance based on reactance (ZPU-XC)
[9 empty] | ZPU-XC |  | = | Xc |  |  |  | x |  | Base kVA
[12 empty] | (Base kV)2 |  |  |  | x |  | 1000
[9 empty] | ZPU-XC |  | = | #REF! |  |  | x |  | #REF!
[12 empty] | #REF! |  |  | x |  | 1000
[9 empty] | ZPU-XC |  | = | #REF!
Total Impedance at (ZL7C2) = Impedance to main bus+Impedance of cable
|  |  |  | ( d ) | Total Impedance
[7 empty] | ZPU-ZL7C2(F7C2) |  |  |  | = | (ZPU-RC)2 |  |  | + |  | (ZPU-XC)2
[7 empty] | ZPU-ZL7C2(F7C2) |  |  |  | = | #REF! |  |  | + |  | #REF!
[7 empty] | ZPU-ZL7C2(F7C2) |  |  |  | = | #REF!
| ( e ) |  | Total per unit impedance thru fault F7C2
|  |  | ZPU-ZT |  | = | ZPU-ST |  |  | + |  | ZPU-ZL1 |  |  | + |  | ZPU-ZL7 |  |  | + | ZPU-ZL7C(F7C) |  |  | + | ZPU-ZL7C2(F7C2)
|  |  | ZPU-ZT |  | = | #REF! |  |  | + |  | #REF! |  |  | + |  | #REF! |  |  | + | #REF! |  |  | + | #REF!
|  |  | ZPU-ZT |  | = | #REF!
|  |  |  | ( f ) | Short Circuit Motor Contribution at 50%
[8 empty] | ZPU-M |  | = | KVA Base
4 x motor kVA
[8 empty] | ZPU-M |  | = | #REF!
[11 empty] | 4 | x | 800
[8 empty] | ZPU-M |  | = |  | #REF!
|  |  |  | ( g ) | Total Impedance to main bus of MCC-1 (ZPU-B(F7C2))
[8 empty] | ZPU-B(F7C2) |  |  | = | ZPU-ZT |  |  | x |  | ZPU-M
[12 empty] | ZPU-ZT |  |  | + |  | ZPU-M
[8 empty] | ZPU-B(F7C2) |  |  | = | #REF! |  |  | x |  | #REF!
[12 empty] | #REF! |  |  | + |  | #REF!
[8 empty] | ZPU-B(F7C2) |  |  | = | #REF!
|  |  |  | ( h ) | ISC AT FAULT CURRENT "F7C2" AT MCC-1
[8 empty] | ISCF7C2(S) |  |  | = | Base Ampere
ZPU-B(F7C2)
[8 empty] | ISCF7C2(S) |  |  |  | 0
#REF!
[8 empty] | ISCF7C2(S) |  |  | = |  | #REF! |  |  |  |  | Ampere
|  |  |  | ( i ) | TAKING INTO CONSIDERATION FOR ASYMMETRICAL
ISC AT FAULT CURRENT "F7C2" AT MCC-1
[8 empty] | ISCF7C2(A) |  |  | = | ISCF7C2(S) |  |  | x |  | 1.25
[8 empty] | ISCF7C2(A) |  |  | = | #REF! |  |  | x |  | 1.25
[8 empty] | ISCF7C2(A) |  |  | = |  | #REF! |  |  |  |  | Ampere
USE * 36 KA INTERRUPTING CAPACITY FOR MAIN BREAKER OF MCC-1
IX
IMPEDANCE DIAGRAM:
[11 empty] | ZS | = | #REF!
[11 empty] | ZT2 | = | Z TRANSFORMER T2 @ 6% | [6 empty] | #REF!
[11 empty] | ZL1 | = | #REF!
[11 empty] | ZL7 |  | = | #REF!
[11 empty] | ZL7C |  | = | #REF!
ZL7C3
[11 empty] | F7C3 |  | (FAULT AT F7C3 PANELBOARD MCC-2)
CABLE IMPEDANCE (FOR LENGTH OF CABLE FROM MAIN BUS TO FAULT (F7C2)
|  | CABLE SIZE IS |  |  |  | 2 |  | SETS 4C X 185mm2 + 95mm2 XLPE/PVC COPPER CABLE
|  | LENGTH OF Cable | [6 empty] | = | 15 |  |  | METERS
|  |  |  | (Cable Resistance) Rc | [6 empty] | = | Cable Resistance | [7 empty] | Length of Cable (KM)
Sets of Cable
|  |  |  | (Cable Resistance) Rc | [6 empty] | = | #REF! | [7 empty] | 0.015
2
|  |  |  | (Cable Resistance) Rc | [6 empty] | = | #REF! |  |  |  | OHMS
|  |  |  | (Cable Reactance) Xc | [6 empty] | = | Cable Reactance | [7 empty] | Length of Cable (KM)
Sets of Cable
|  |  |  | (Cable Reactance) Xc | [6 empty] | = | #REF! | [7 empty] | 0.015
2
|  |  |  | (Cable Reactance) Xc | [6 empty] | = | #REF! |  |  |  | OHMS
|  |  |  | ( a ) | Total Impedance
[8 empty] | ZL7C3 |  |  | = | (ZPU-RC)2 |  |  | + |  | (ZPU-XC)2
[8 empty] | ZL7C3 |  |  | = | #REF! |  |  | + |  | #REF!
[8 empty] | ZL7C3 |  |  | = | #REF!
|  |  |  | ( b ) | Total Impedance based on resistance (ZPU-RC)
[9 empty] | ZPU-RC |  | = | Rc |  |  |  | x |  | Base kVA
[12 empty] | (Base kV)2 |  |  |  | x |  | 1000
[9 empty] | ZPU-RC |  | = | #REF! |  |  | x |  | #REF!
[12 empty] | #REF! |  |  | x |  | 1000
[9 empty] | ZPU-RC |  | = | #REF!
|  |  |  | ( c ) | Total Impedance based on reactance (ZPU-XC)
[9 empty] | ZPU-XC |  | = | Xc |  |  |  | x |  | Base kVA
[12 empty] | (Base kV)2 |  |  |  | x |  | 1000
[9 empty] | ZPU-XC |  | = | #REF! |  |  | x |  | #REF!
[12 empty] | #REF! |  |  | x |  | 1000
[9 empty] | ZPU-XC |  | = | #REF!
Total Impedance at (ZL7C3) = Impedance to main bus+Impedance of cable
|  |  |  | ( d ) | Total Impedance
[7 empty] | ZPU-ZL7C3(F7C3) |  |  |  | = | (ZPU-RC)2 |  |  | + |  | (ZPU-XC)2
[7 empty] | ZPU-ZL7C3(F7C3) |  |  |  | = | #REF! |  |  | + |  | #REF!
[7 empty] | ZPU-ZL7C3(F7C3) |  |  |  | = | #REF!
| ( e ) |  | Total per unit impedance thru fault F7C3
|  |  | ZPU-ZT |  | = | ZPU-ST |  |  | + |  | ZPU-ZL1 |  |  | + |  | ZPU-ZL7 |  |  | + | ZPU-ZL7C(F7C) |  |  | + | ZPU-ZL7C3(F7C3)
|  |  | ZPU-ZT |  | = | #REF! |  |  | + |  | #REF! |  |  | + |  | #REF! |  |  | + | #REF! |  |  | + | #REF!
|  |  | ZPU-ZT |  | = | #REF!
|  |  |  | ( f ) | Short Circuit Motor Contribution at 50%
[8 empty] | ZPU-M |  | = | KVA Base
4 x motor kVA
[8 empty] | ZPU-M |  | = | #REF!
[11 empty] | 4 | x | 800
[8 empty] | ZPU-M |  | = |  | #REF!
|  |  |  | ( g ) | Total Impedance to main bus of MCC-2 (ZPU-B(F7C3))
[8 empty] | ZPU-B(F7C3) |  |  | = | ZPU-ZT |  |  | x |  | ZPU-M
[12 empty] | ZPU-ZT |  |  | + |  | ZPU-M
[8 empty] | ZPU-B(F7C3) |  |  | = | #REF! |  |  | x |  | #REF!
[12 empty] | #REF! |  |  | + |  | #REF!
[8 empty] | ZPU-B(F7C3) |  |  | = | #REF!
|  |  |  | ( h ) | ISC AT FAULT CURRENT "F7C3" AT MCC-2
[8 empty] | ISCF7C3(S) |  |  | = | Base Ampere
ZPU-B(F7C3)
[8 empty] | ISCF7C3(S) |  |  |  | 0
#REF!
[8 empty] | ISCF7C3(S) |  |  | = |  | #REF! |  |  |  |  | Ampere
|  |  |  | ( i ) | TAKING INTO CONSIDERATION FOR ASYMMETRICAL
ISC AT FAULT CURRENT "F7C3" AT MCC-2
[8 empty] | ISCF7C3(A) |  |  | = | ISCF7C3(S) |  |  | x |  | 1.25
[8 empty] | ISCF7C3(A) |  |  | = | #REF! |  |  | x |  | 1.25
[8 empty] | ISCF7C3(A) |  |  | = |  | #REF! |  |  |  |  | Ampere
USE * 36 KA INTERRUPTING CAPACITY FOR MAIN BREAKER OF MCC-2
Isc

## DATA_BASE
Data Base-1 | Data Base-2 | Data Base-3 |  | Data Base-4 (as per SEC Standard)
Cable MM2 | XFMR KVA | Standard KA Ratings |  | TR Rating (KVA) | TR Losses (W) | % ZTR | KA Rating | No. of 1Cx630mm2 cables per phase
10 | 50 | KA | Catalog | 300 | 3200 | 4 | 25 | 2
16 | 100 | 10 | M/MG | 500 | 4700 | 5 | 25 | 2
25 | 160 | 14 | W | 1000 | 9000 | 6 | 25 | 2
35 | 200 | 15 | M/MG | 1500 | 14000 | 6 | 40 | 4
50 | 250 | 18 | M/MG
70 | 300 | 21 | SEC
95 | 315 | 22 | MG/W
120 | 400 | 25 | SEC
150 | 500 | 30 | M/MG/W
185 | 630 | 35 | M/MG/W
240 | 800 | 40 | SEC
300 | 1000 | 42 | MG/W
630 | 1250 | 50 | M/MG/W
| 1500 | 60 | M
| 1600 | 65 | M/MG/W
| 2000 | 70 | MG
| 2500 | 75 | MG
| 3150 | 85 | M/MG
| 4000 | 100 | MG/W
|  | 125 | M/W
|  | 130 | MG
|  | 150 | MG
BMR/Jan.12, 2005